Building a PiJack box

Start with a OEM version of the Labjack U3.
3D print one of our boxes. The .stl file for the box can be found on the network drive under /reference/internal/PiJack

+5v

2.2k
2.2k

To current sensor

FIOx

Cut 6 ft. lengths of the hookup wire,

FIOx

56k
2.2k

To test point
one piece of
Brown,
Red and
Orange
Two pieces of
Yellow
Green
Blue
Violet
White
and 3 lengths of the 3-wire gray cable for the current sensors. Strip back about 4” of the outer gray sheathing on the current sensor cables, so the wires will fit through the cable glands.

Solder a 56K precision resistor to the end of each colored piece of hookup wire.
For the 3 Current sensor cables, solder a 2.2K precision resistor to the end of the green wire.
Put heat-shrink tubing over the connections

Three current sensors connect to the FIO0-FIO2 inputs on the circuit board.
Solder a 2.2k resistor in parallel with a 10uf capacitor for each current sensor (3x)Bend them to fit between the FIO input line and ground, but solder only the ground side.
Insert the 2.2k resistor attached to the cable into the corresponding FIO input line and now solder both resistors to that input. Solder the red wires to +5v and black to gnd.

All the other FIO lines should have the 56K resistor soldered to the input, plus a 2.2k between the input and ground, like in the photo.
Colors are:
FIO3 Yellow
FIO4 Green
FIO5 Blue
FIO6 Violet
FIO7 White

Stand 8 of the 2.2k precision resistors in the DB15 connector holes 4,5,6,7 and 12,13, 14 & 15. Solder them in place. Connect the leads which are sticking up all together to hole 8, which is gnd.

Connect the colored hookup wires with 56K resistors on the end to J2:
Hole Color
8	Brown
9	Red
10	Orange
11	Yellow
12	Green
13	Blue
14	Violet
15	White

Run these wires out through the gland labeled “E”
Run the other wires including the current sensor cables out through the gland labeled “F”

Trim the USB cable down to about 10”, removing the “B” connector. Run the wire through the hole in the side of the case and solder to the U3 as shown. Put a cable tie around the USB wire inside the box to act as a strain relief. Close up the box. – Done